SCOPE OF SERVICE

General Information:

Qatar Electricity & Water Company (QEWC) is considered to be a forerunner among private sector companies involved in the field of Power Generation and Water Desalination in the Gulf region.

QEWC currently owns and operates following plants at its Ras Abu Fontas Stations:

- RAF-B & B2 Power and Desalination Plants.

- RAF-A1 & A2 Desalination Plants.

QEWC plans to award diving contract for Three  Years to any of the local diving companies based in Qatar. The diving company shall carry out work as detailed in the attached Schedule of Prices.

RAF-B  & B2 Power and Desalination Plants:

Sea water is supplied to Ras Abu Fontas-B Power Station from four off-shore intake points and for B2 station, from three intake points located approx. 2 km away from Seawater Pump House through four GRP intake pipes; each one is of 1900 mm in diameter, 22.75 mm total thickness and are placed approx. 9 meters under the sea level. The Intake pipe consists of a number of pipes. Each pipe has 12 m length, which are connected by means of a double bell coupling joint.

All (B & B2) intake pipes are connected to common intake chamber, which is connected to individual pump chambers. In the event of working on any of the intake pipes, this can be isolated by means of stop-logs.

Each intake pipe is provided with 800 mm manhole located at each 100 meter. There is 4’’ HDPE chlorine dozing lines outside the intake pipes along its length, installed on the sea bed, 2 nos. each for RAF-B & RAF-B2 station.

These Chlorine dosing lines are to be inspected and if required to be repaired.

This chlorine dozing system usually requires acid cleaning for every 3 months in order to ensure the cleanliness of the system. Divers required to inspect the lines before and after the acid cleaning and if required to be repaired.

Screening system consists of Drum screens and Racking screens which needs annual inspection of screen pit and debris cleaning from inside the pit using air ejectors.

RAF-B consists of 3 nos. of drum screens and 6 nos. of racking screens, RAF-B2 consists of 2 nos. of drum screens and 4 nos. of racking screens.

Pump house consists of ten main pumps (B & B2). Each pump is provided with a separate cell which facilitates independent system isolation for each pump. This system may also require inspection.

The Intake System of RAF-B & B2 is provided with Oil Boom System. The system consist of Buoys, chains and solar lights.

RAF-A1 Desalination Plant:

Sea water is supplied to Ras Abu Fontas A1 Power Station from four off-shore intake points located approx. 2 km away from Seawater Pump House through four GRP intake pipes, each one of 1900 mm in diameter, 22.75 mm total thickness and are placed approx. 9 meters under the sea level. The Intake pipe consists of a number of pipes, each pipe of 12 m length, which are connected by means of a double bell coupling joint.

All four intake pipes are connected to common intake chamber, which is connected               to individual pump chambers. In the event of working on any of the intake pipes, this can be isolated by means of stop-logs.

Each intake pipe is provided with 800 mm manhole located at each 100 meters. There is 6’’ GRP chlorine line inside each of intake pipes along its length. The chlorine line is internally mounted on the main pipe by means of GRP clamp laminated on the surface of Main Pipe.

Intake pipes and Chlorine dosing are required to be inspected and if required to be repaired. Also the intake screening system requires inspection during isolation.

Screening system consists of 3 nos. of Traveling band screens and Racking screens which needs inspection of screen pit in case of emergency. In the event of working on any travelling band screens, this can be isolated individually by means of motorized penstocks.

RAF-A2 Desalination Station:

Sea water is supplied to Ras Abu Fontas (A2) Power Station from Two off-shore intake points located approx. 2 km away from Seawater Pump House through Two GRP intake pipes each one has 2500 mm in diameter are placed approx. 9 meters under the sea level.

All two intake pipes connected to common intake chamber, which is connected to individual pump chambers. In the event of working on any of the intake pipes, this can be isolated by means of stop-logs.

Each intake pipes provided with 800 mm manhole located at each 200 meters. There are 3’’ HDPE chlorine dozing lines outside the intake pipes along its length, installed on the sea bed, each line dozing to respective intake pipe.

These Chlorine dosing lines are to be inspected and if required to be repaired.

This chlorine dozing system usually requires acid cleaning for every 3 months in order to ensure the cleanliness of the system. Divers required to inspect the lines before and after the acid cleaning and to be repaired if required.

Contractor Scope of Work

- Removal of all debris, seashells, barnacles, sea growth, sea weeds etc. and whatever debris accessible which could obstruct the seawater flow at the Strainers installed under the sea level.

- Submitting of Photographic report showing the strainers condition before and after the cleaning activities (still photographs shall be of good quality and time and date stamped on the photographs).

- Submitting of a Video Photographic Report showing the strainers condition before and after the cleaning activities. Video shall be recorded on VCD and submitted to QEWC.

- 8 working hours per day.

- The seawater intake strainers cleaning.

- The contractor shall carry out inspection for the polyethylene Chlorine line. Take relevant photographs to show any damages to QEWC and support to attend the defect (QEWC will provide all the required materials) .

- Work to be completed by the divers as per QEWC Schedule.

General Requirements:

- Contractor shall provide sufficient qualified, experienced and competent manpower to carry out the work as detailed in the Schedule of Prices.

- Contractor is responsible to carry out the work in a safe way and to the satisfaction of QEWC by the use of available drawing and information at site.

- Contractor is responsible to provide the required gears for the diving activities to carry out the work in safe manner.

- Communication between the diver and the staff on the boat shall be within the scope of the Contractor.

- Contractor shall have the necessary Insurance Coverage for all the staff engaged in carrying out the work.

- Minimum of one set of qualified Diver required to carry out any activites inside the station . 3 divers & 1 Supervisor shall be deployed (two in the sea and one on the boat) to carry out the work.

- Stand-by Divers(2 Nos)  for the Works which carried out by QEWC in the Pump Pits, Drum Screens areas etc

- The Contractor shall work within the safety rules & permit system of QEWC.

- Contractor is wholly solely responsible for the safety of their staff.

Others General Requirements:

- Method Statement and Risk assessment shall be submitted by the contractor to get approval from QEWC safety section before starting any specific job.

- Whenever required by QEWC, supplier to submit report about the progress of ongoing work to QEWC. Contractor shall produce the underwater video and still photography from time to time during the course of work.

- The Contractor shall submit, whenever required, the final report of all the activities done with still and video documentation.

Isolation Activities and Work Permit:

- In case of Intake lines inspection, the intake line shall be isolated by QEWC. Divers shall assist QEWC in doing so, whenever there may be a requirement of cleaning the stop-log tracks.

- Penstock tracks cleaning activities shall be confirmed by the penstock isolation.

- All relevant permits shall be taken by the Contractor and the instruction from QEWC Engineer In-charge shall be taken by the Contractor before starting any job.

Other Important Requirements:

- The prices quoted shall include all aspects of the work and shall cover all obligations of the Contractor in carrying out the same.

- Working hours shall be dependent on the site conditions.

- The Contractor’s divers shall be well experienced, qualified and certified.

- The divers CVs are to be given to QEWC for review and approval.

- The work shall be done and completed by the contractor irrespective of the weather conditions and tide etc. even if they are adverse, unless this will result in compromising the safety of the divers.

- The rates shall include mobilization and demobilization of manpower and equipment required, to and from the site, on daily basis

- All necessary arrangement and reporting to the site to be done by contractor on 48 hour notice period in case of none critical work.

- All necessary arrangements and reporting to the site to be done by contractor on 6 hours’ notice period in case of critical work at RAF station

Scope of Supply

Following shall be supplied by the Contractor

- All necessary manpower and supervision for the work

- All special Diving tools and diving gears for the divers

- All relevant Diving tools and tackles

- All diving related consumables

- All consumable related to still and video photography

- QEWC will provide all underwater repair material. In case of required material not available with QEWC, Contractor can provide the offer.

- Oxygen refill cylinders.

This is a prequalification document. Prices must not be mentioned anywhere in the prequalification submission.